## Summary Calculations
Overview |  | Water Balance
| This water and nutrience balance spreadsheet has been developed for the purpose of providing guidance to applicants seeking to install or renew wastewater management systems on Lord Howe Island (LHI). | How many Bedrooms does the infrastructure contain?
| The Spreadsheet has been debveloped by the Lord Howe Island Board (LHIB) to be consistent with the Wasterwater Management Strategy for LHI. | 1 | 0 | Bedrooms
| The information contained in this spreadsheed does not prevent the LHIB from requesting additional information and calculations in relation to the effluent management syetem at the LHIB's discression. |  | 0 | Litres/day
Instructions |  | What is the minimum number of tourist that the system serivces?
Please fill in all green cells including: |  | 2 | 0 | Persons
1 | Number of bedrooms the wastewater management system is proposed to service. |  | 0 | Litres/Day
2 | The total capacity of tourists that the wastewater management system will service. | Do you have any additional hydraulic load on the system (transit room, restaurant, commercial fittings, ect)?
3 | Catcultated additional hydraulic load created by activities that are ancillary or separate to residential or tourist accomodation. Note that detailed calculations need to be provided, demonstrating the method for calculating the dditional loads. | 3 |  | Litres/Day
4 | Select the soil type from the drop down list. Soil types need to be demonstrated with photographic evidence. | Your total Hydraulic load is:
5 | Input the name and brand of the proposed system. |  | 0 | Litres/Day
6 | Input the effluent nitrogen (N) concentration (from supplier).
7 | Input the effluent phospherous (P) concentration (from supplier).
8 | Input the design life of the system (from supplier). | What Soil type is your irrigation area? |  | Daily DPR | Rainfall Co | Bulk Denisity | P-sorption result
9 | From the dropdown list, select the vegetation types where the irrigation area is proposed. Where effluent disposal is proposed in the SNV, a construction management plan may be required. | 4 | Sand | 5 | 0.8 | 1.8 | 170
| The area required for the irrigation area is taken as the highest limiting factor from water balance, nitrogen and phospherous calculations. | Area required for water balance:
|  |  | 0 | Square metres
Nutrient Balance
System type
5
Effluent Value
|  | 6 | 20 | Effluent N Concentration
|  | 7 | 2 | Effluent P Concentration
|  | 8 | 40 | Design Life of System
Vegetation of Irrigation area
|  | 9 | Significant natural vegetation | 200 | 20
Area according to limiting factor
|  |  | 0 | Water Balance
|  |  | 0 | Nitrogen
|  |  | 0 | Phosphorus
Area required
|  |  | 0 | Square metres

## Water Balance
Nominated Area Water Balance & Storage Calculations
Site Address:
[13 empty] | OCCUPANCY |  |  |  | SOILS
INPUT DATA | [12 empty] | Flow Allowance |  | 120 | L/p/d | LHI Soils | Column1 | Daily DPR | units | Effective rainfall | Column2 | units3 | Bulk denisity | Phospurus sorpion
Design Wastewater Flow | Q | 0 | L/day | [9 empty] | No. of bedrooms |  | 0 |  | Sand |  | 5 | mm/day | 0.8 |  | number | 1.8 | 170
Daily Design Percolation Rate | DPR | 5 | mm/day | Equivalent to litres per m2 per day - based on LHI Strategy for secondary effluent | [8 empty] | Occupancy |  | 0 | Beds + 1 | Calcareous earth |  | 4 | mm/day | 0.75 |  | number | 1.6 | 400
Nominated Land Application Area | L | 2404 | m2 | [9 empty] | Design Flow |  | 0 | L/d | Volcanic soil |  | 3 | mm/day | 0.7 |  | number | 1.4 | 700
Crop Factor | C | 0.7-0.8 | unitless | Estimates evapotranspiration as a fraction of pan evaporation; varies with season and crop type
Effective Rainfall/Runoff Coefficient | RC | 0.8 | unitless | Proportion of rainfall that remains onsite and infiltrates; function of slope/cover, allowing for any runoff | [20 empty] | Sand
Rainfall Data | Lord Howe Island Aero BoM 200839 |  |  | Mean Monthly Data | [20 empty] | Calcareous earth
Evaporation Data | Norfolk Island BoM 200288 |  |  | Mean Monthly Data | [20 empty] | Volcanic soil
Parameter | Symbol | Formula | Units | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Days in month | D | \ | days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | 365
Rainfall | R | \ | mm/month | 117.5 | 116.2 | 134.9 | 134.2 | 157.7 | 173.1 | 141 | 107.7 | 110.7 | 106.1 | 110.3 | 102.4 | 1511.8
Evaporation | E | \ | mm/month | 167.4 | 148.4 | 151.9 | 120 | 102.3 | 90 | 93 | 105.4 | 117 | 139.5 | 153 | 170.5 | 1558.4
Daily Evaporation |  |  | mm/day | 5.4 | 5.3 | 4.9 | 4 | 3.3 | 3 | 3 | 3.4 | 3.9 | 4.5 | 5.1 | 5.5
Crop Factor | C |  | unitless | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8
OUTPUTS
Evapotranspiration | ET | ExC | mm/month | 133.92 | 118.72 | 121.52 | 84 | 71.61 | 63 | 65.1 | 73.78 | 81.9 | 111.6 | 122.4 | 136.4 | 1183.95
Percolation | B | (DPR/7)xD | mm/month | 155 | 140 | 155 | 150 | 155 | 150 | 155 | 155 | 150 | 155 | 150 | 155 | 1825
Outputs |  | ET+B | mm/month | 288.92 | 258.72 | 276.52 | 234 | 226.61 | 213 | 220.1 | 228.78 | 231.9 | 266.6 | 272.4 | 291.4 | 3008.95
INPUTS
Retained Rainfall | RR | RC | mm/month | 94 | 92.96 | 107.92 | 107.36 | 126.16 | 138.48 | 112.8 | 86.16 | 88.56 | 84.88 | 88.24 | 81.92 | 1209.44
Effluent Irrigation | W | (QxD)/L | mm/month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  | RR+W | mm/month | 94 | 92.96 | 107.92 | 107.36 | 126.16 | 138.48 | 112.8 | 86.16 | 88.56 | 84.88 | 88.24 | 81.92 | 1209.44
STORAGE CALCULATION
Storage remaining from previous month |  |  | mm/month | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage for the month | S | (RR+W)-(ET+B) | mm/month | -194.92 | -165.76 | -168.6 | -126.64 | -100.45 | -74.52 | -107.3 | -142.62 | -143.34 | -181.72 | -184.16 | -209.48
Cumulative Storage | M |  | mm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Storage for Nominated Area | N |  | mm | Mean Monthly Data Jan: 0
| V | NxL | L | Mean Monthly Data Jan: 0
LAND AREA REQUIRED FOR ZERO STORAGE |  |  | m2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MINIMUM AREA REQUIRED FOR ZERO STORAGE: |  |  |  | Mean Monthly Data Jan: 0; Mean Monthly Data Mar: m2
1. Enter the property address in Cell B2.
2. For domestic premises, determine number of bedrooms and enter number in Cell P5. This will then calculate the daily design wastewater flow on the basis of occupancy of two persons for the first bedroom and one person for each subsequent bedroom. The daily hydraulic load will then be displayed in Cell Q6. This value should then be transferred to Cell C4.
3. For non-domestic premises determine the daily hydrauic load. This value should represent maximum potential occupancy and should take into consideration all possible wastewater generating activities. For non-domestic premises this value should be transferred to Cell C4.
4. Determine the soil type in the proposed land application area. Depending on the soil type, select the appropriate value for Daily Design Percolation Rate (Daily DPR) from Cells U4, U5 or U6. Enter the selected Daily DPR value in Cell C5.
5. Again depending on the soil type, select the appropriate value for Effective Rainfall (Rainfall Runoff Coefficient) from Cells W4, W5 or W6. Enter the selected Rainfall Runoff Coefficient value in Cell C8.
6. Mean monthly rainfall data for Lord Howe Island Aero and daily evaporation data for Norfolk Island are used in the water balance spreadsheet. The spreadsheet is already populated with these values.
7. The spreadsheet is also already populated with appropriate Crop Factor values used to convert Evaporation data to Evapotranspiration.
8. The spreadsheet automatically calculates the land application area required to avoid the need for wet weather storage in all months. This is the maximum value of Cells E33 to P33. This value should be inserted in Cell C6. If this area cannot be achieved, it is possible to enter lesser values in Cell C6, in which case the words "Storage Required" appear in Cell E35 and the required "wet weather" storage volume will be shown in Cell E32.

## Nutrient Balance
Nutrient Balance
Site Address: | Somerset Secondary System
Please read the attached notes before using this spreadsheet.
SUMMARY - LAND APPLICATION AREA REQUIRED BASED ON THE MOST LIMITING BALANCE = | [7 empty] | 0 | m2
INPUT DATA [1] | [9 empty] | EFFLUENT NUTRIENT CONCENTRATION
Wastewater Loading |  |  |  | Nutrient Crop Uptake | [5 empty] | System type |  |  | Nitrogen | Phosphorus | units
Hydraulic Load |  | 0 | L/Day | Crop N Uptake | 200 | kg/ha/yr | which equals | 54.7945 | mg/m2/day | Secondary treatment (AWTS) |  |  | 30 | 10 | mg/L
Effluent N Concentration |  | 20 | mg/L | Crop P Uptake | 20 | kg/ha/yr | which equals | 5.4795 | mg/m2/day | Fuji Clean CE1500EX |  |  | 18.11 | 1.33 | mg/L
% Lost to Soil Processes (Geary & Gardner 1996) |  | 0.2 | Decimal | Phosphorus Sorption | [5 empty] | Fuji Clean CRX1500 |  |  | 8.29 | 0.24 | mg/L
Total N Loss to Soil |  | 0 | mg/day | P-sorption result | 170 | mg/kg | which equals | 1530 | kg/ha | Rootzone Model 1200 |  |  | 20 | 10 | mg/L
Remaining N Load after soil loss |  | 0 | mg/day | Bulk Density | 1.8 | g/cm3
Effluent P Concentration |  | 2 | mg/L | Depth of Soil | 0.5 | m
Design Life of System |  | 40 | yrs | % of Predicted P-sorp.[2] | 0.5 | Decimal
METHOD 1: NUTRIENT BALANCE BASED ON ANNUAL CROP UPTAKE RATES | [9 empty] | CROP NUTRIENT UPTAKE
Minimum Area required with zero buffer |  |  | Determination of Buffer Zone Size for a Nominated Land Application Area (LAA) | [6 empty] | Vegetation type | Column1 | Column2 | Nitrogen | Phosphorus | units
Nitrogen | 0 | m2 | Nominated LAA Size |  |  | 0 | m2 |  |  | Kikuyu |  |  | 260 | 25 | kg/ha/yr | Kikuyu
Phosphorus | 0 | m2 | Predicted N Export from LAA |  |  | 0 | kg/year |  |  | Significant natural vegetation |  |  | 200 | 20 | kg/ha/yr | Significant natural vegetation
|  |  | Predicted P Export from LAA |  |  | 0 | kg/year |  |  | Coastal rainforest |  |  | 200 | 20 | kg/ha/yr | Coastal rainforest
|  |  | Phosphorus Longevity for LAA |  |  | #DIV/0! | Years |  |  | Kentia palm plantation |  |  | 200 | 20 | kg/ha/yr | Kentia palm plantation
|  |  | Minimum Buffer Required for excess nutrient |  |  | 0 | m2
PHOSPHORUS BALANCE
STEP 1: Using the nominated LAA Size | [9 empty] | SOIL PHOSPHORUS SORPTION
Nominated LAA Size | 0 | m2 | [7 empty] | LHI Soils | Column1 | P-sorption | Column2 | units
Daily P Load | 0 | kg/day |  | Phosphorus generated over life of system |  |  | 0 | kg |  | Sand |  | 170 |  | mg/kg
Daily Uptake | 0 | kg/day |  | Phosphorus vegetative uptake for life of system |  |  | 0.08 | kg/m2 |  | Calcareous earth |  | 400 |  | mg/kg
Measured p-sorption capacity | 0.153 | kg/m2 | [7 empty] | Volcanic soil |  | 700 |  | mg/kg
Assumed p-sorption capacity | 0.0765 | kg/m2 |  | Phosphorus adsorbed in 50 years |  |  | 0.0765 | kg/m2 |  | Based on analysis of LHI soils 2014
Site P-sorption capacity | 0 | kg |  | Desired Annual P Application Rate |  |  | 0 | kg/year
[6 empty] | which equals | 0 | kg/day |  | SOIL BULK DENSITY
P-load to be sorbed | 0 | kg/year | [7 empty] | LHI Soils | Column1 | Bulk Density | Column2 | units
[10 empty] | Sand |  | 1.8 |  | g/cm3
[10 empty] | Calcareous earth |  | 1.6 |  | g/cm3
[10 empty] | Volcanic soil |  | 1.4 |  | g/cm3
NOTES
[1]. Model sensitivity to input parameters will affect the accuracy of the result obtained. Where possible site specific data should be used. Otherwise data should be obtained from a reliable source such as, - Environment and Health Protection Guidelines: Onsite Sewage Management for Single Households - Appropriate Peer Reviewed Papers - EPA Guidelines for Effluent Irrigation - USEPA Onsite Systems Manual.
[2]. Conservative estimate based on work by Geary & Gardner (1996) and Patterson (2002).
[3]. A multiplier, normally between 0.25 and 0.75, is used to estimate actual P-sorption under field conditions which is assumed to be less than laboratory estimates.
1. Select the appropriate effluent nutrient concentration for the chosen treatment system type and enter the respective values for nitrogen and phosphorus in Cells C9 and C13.
2. Select the appropriate crop nutrient uptake rates for the vegetation type in the land application area and enter the respective values for nitrogen and phosphorus in Cells G8 and G9.
3. Select the appropriate soil phosphorus sorption value for the soil type in the land application area and enter the value in Cell G11.
4. Select the appropriate soil bulk density value for the soil type in the land application area and enter the value in Cell G12.
5. Set the appropriate depth of soil in the land application area in Cell G13. It is recommended that this depth not exceed 0.8 metres unless site specific data has been obtained and the soil is of uniform character for the whole depth of the soil.
6. The minimum required land application area to meet the requirements of the water and nutrient balance is identified in Cell J4.

## Sheet2
0 | pax
150 | EP
0 | T